## Slide 1: Grid-following Voltage Source Converter : modelling under phasor approximation and simulation results on the 4-VSC test system
Thierry Van Cutsem
thierry.h.van.cutsem@gmail.com
https://thierryvancutsem.github.io/home/
March 28, 2024

## Slide 2: Motivation and objectives
Power-electronics converters push the phasor approximation to its limit (and beyond…)
There is a need for benchmark systems
  with large penetration of converters
  small enough to be easily tractable
  complex enough to reflect real-life systems
  easily implemented in various simulation tools
A 100% power electronics, 4-VSC test system is presented
The embedded EMT models of VSCs were developed, tuned and thoroughly tested by Prof. Xavier Guillaud and his team at Ecole Centrale de Lille, France
  this presentation focuses on models under the phasor (or “RMS”) approximation
  simulation results in phasor-mode are compared with their EMT counterparts

## Slide 3: Motivation and objectives
Models and data of the benchmark are available in open source
This is not a presentation about the “best” design and/or tuning of VSC controls
  the generic models in this presentation are generic
  they encompass many variants proposed in the literature

## Slide 4: Table of contents
Motivation and objectives
Modelling of the grid-following VSC
Examples of simulations in the 4-VSC system
Comparison with EMT simulations

## Slide 5: Grid-following VSC model: basic assumptions
MMC-type converter connected to grid through transformer.
  no LC filter
DC side not modelled ( assumed constant)
  focus is on AC grid dynamics

## Slide 6: Grid-following VSC model: reference frames
Network reference frame :
axes rotating at angular speed (rad/s)
: rectangular components of PCC voltage phasor .
VSC control reference frame :
axes tracking the voltage phasor and given by Phase Locked Loop
: components of
: phase angle of wrt (rad) : angle between and (rad) in steady-state : =
: angular speed of axes (pu/s)
: nominal angular frequency (in rad/s)

## Slide 7: Grid-following VSC model: voltages and currents in transformer
Passing from to reference frame :
voltage at PCC : current in converter :
Dynamics of current in transformer in reference frame :
  differential equations not in agreement with the phasor approximation of network (algebraic eqs.)
  aimed at (hopefully) capturing fast dynamics of converter

## Slide 8
Blocking/unblocking the PLL for low voltage :
V : PCC voltage magnitude (pu) = 0.4 pu = 0.5 pu
values in per unit on the Snom base (nominal apparent power of converter)
Grid-following VSC model: Phase Locked Loop (PLL)

## Slide 9: Grid-following VSC model: d-q current control
= 6 pu/s = 0.4584 for WP1 and WP2
= 0.5730 for HVDC1 and HVDC2
= 1200 rad/s)

## Slide 10: Grid-following VSC model: active power control
= 1/300 = 3.3 ms = 10 pu/s = 10/300 = 0.0333
: maximum allowed current = nominal current = 1 pu (could be slightly > 1 as well)
Lower block-diagram : limits the rate of recovery of after it has been decreased by an increase of
(priority is given to the reactive current)
T : small time constant (0.002 s) = 0.5 pu/s for WP1 and WP2
= 10 pu/s for HVD1 and HVDC2

## Slide 11: Grid-following VSC model: voltage / reactive power control
: reactive power injected into the grid (pu)
3.3 ms
: compensated voltage :
and the voltage magnitude is controlled
vqswitch = 1 : = 50 pu/s = = 0.1667
vqswitch = 0 : = 10 pu/s = = 0.0333
Alternative choices are presented in the next slide.
Dynamic voltage support : not considered (.

## Slide 12: Grid-following VSC model: limit on quadrature current
Examples of values :
Full current can be used :
: initial active current
specified (e.g. 0.3) :
All values in per unit

## Slide 13: Table of contents
Motivation and objectives
Modelling of the grid-following VSC
Examples of simulations in the 4-VSC system
  glance at simulation tool
  large-disturbance simulation
Comparison with EMT simulations

## Slide 14: STEPSS (Static and Transient Electric Power Systems Simulation)
Power Flow Computation
RApid Multithreaded Simulation of Electric power System
CODE GENerator : translation
of user-defined models

## Slide 15: STEPSS (Static and Transient Electric Power Systems Simulation)
RAMSES
differential/algebraic equations solver developed at the Univ. of Liège by P. Aristidou and T. Van Cutsem
phasor approximation
decomposition (Schur-complement) + localization techniques
parallel processing
CODEGEN
receives user-defined models written according to a simple syntax
translates them into FORTRAN 2003 code, to be compiled and linked to the rest of RAMSES
4 types of models : excitation control of sync. mach. / torque control of sync. mach. / injectors / two-ports
models freely shared by users  open-source simulation software
LICENSE TERMS
  STEPSS can be used free of charge for non-commercial/non-profit purposes, in a version limited to 1000 buses and 2 cores.

## Slide 16: Example: large-disturbance in the 4-VSC system
Operating point No. 1
All VSCs in grid-following mode
  WP1 in reactive power control
  WP2, HVDC1 and HVDC2 in voltage control
short-circuit power of external system : 20 000 MVA
disturbance :
  solid fault on line A-C#1, next to bus A
  cleared in 150 ms by opening line A-C#1

## Slide 17
Network voltages
Example: large-disturbance in the 4-VSC system

## Slide 18: Example: large-disturbance in the 4-VSC system
Active powers and direct-current references

## Slide 19: Example: large-disturbance in the 4-VSC system
Reactive powers and quadrature-current references

## Slide 20: Table of contents
Motivation and objectives
Modelling of the grid-following VSC
Examples of simulations
Comparison with EMT simulations

## Slide 21: Simulation of a mild disturbance at operating point No. 2
All VSCs in grid-following mode
“mild” disturbance: outage (without fault) of lightly loaded circuit A-B
variation of short-circuit power of the external equivalent

## Slide 22: EMT vs. phasor-mode simulations
Phasor approximation
response marginally stable for = 5 500 MVA
oscillation frequency  8 Hz
EMT model
response marginally stable for = 17 700 MVA
oscillation frequency  16 Hz
Voltage of WP2 (pu)

## Slide 23: Simulation of a mild disturbance at (variant of) oper. pt No. 2
Variant without load at bus C (corresponding power taken by external equivalent)
All four converters in grid-following mode
short-circuit power of external equivalent : 17 700 MVA
same disturbance

## Slide 24: EMT vs. phasor-mode simulations
Phasor approximation
EMT model
Damping effect of (constant admittance) load not seen in phasor-mode simulation
Voltage of WP2 (pu)