## Test-cases
test ID | Test system | short description | variants | voltage levels (KV) | AC/DC | number of buses | number of generators | load (MW,MVAR) | type of stability | academic criteria | operation criteria | dynamics of interest | event | modelling details (component details are given in the component models sheet) | RMS available implementations | EMT implementations | Implementation issues | references
1 | WSCC 9 | modified version of the Western System Coordinated Council 9 Bus test case, this test system is a well-known system used for transient stability analysis |  | 13,8 ; 16,5; 18; 230 | ac | 9 | 3 | 315;115 | transient stability |  |  | ms to some sec | three phase fault | synchronous generator RL load | dynawo : https://github.com/dynawo/dynawo/tree/master/examples/DynaSwing/WSCC9/WSCC9_Fault Powerfactory | DPsim: https://github.com/sogno-platform/dpsim/blob/master/dpsim/examples/cxx/CIM/EMT_WSCC-9bus_FullOrderSG.cpp Powerfactory |  | REF1-REF4
2 | IEEE 14 | simplified model of the American Electric Power System utilized in the Midwestern United States since 1962 |  |  | ac | 14 | 2 generators, 3 condensers |  | transient stability |  |  | ms to some sec | three phase fault | synchronous generator, condenser two winding transformers three winding transformers PQ, alpha-beta load | dynawo: https://github.com/dynawo/dynawo/tree/master/examples/DynaSwing/IEEE14/IEEE14_Fault Powerfactory (DPsim) | Powerfactory (DPsim) |  | REF1-REF4
3 | IEEE 39 | renowned New England 10 generator power system, and it has been utilized to address small-signal stability in conventional power systems |  | 345 | ac | 39 | 10 | 6097; 1409 | small signal stability, and frequency response, trnasient stability |  |  | ms to some sec |  | synchronous generator RL load | Powerfactory (DPsim) | Powerfactory (DPsim) |  | REF1-REF4
4 | IEEE 118 | Since 1962, this test system has been a part of the American Electric Grid. |  |  | ac |  |  |  | voltage stability
5 | CIGRE B4 DC | This test system was developed by CIGRE B4 Working Group (WG) for dc system studies. The test case includes two onshore ac systems, four offshore ac systems, two dc nodes with no connection to ac systems, and three interconnected dc systems |  | 400;200;380;145 | dc | 26 |  | 7500, NA |  |  |  | ms to minutes |  | three interconnected dc systems: - DCS1 two terminal symmetric monopole HVDC link with +-200kV - DCS2 4 terminal symmetric monopole HVDC link - DCS3 five terminal, bipole HVDC meshed grid with +-400kV - mix of DC cable and overhoead lines, AC lines - AC/DC converters, DC/DC converters - voltage source, WTG |  |  |  | REF5
6 | CIGRE MV | resources in medium-voltage (MV) 20-kV distribution systems. proposed by CIGRE WG C6-04 for distributed resources and storage-coordinated control, energy management, protection and fault ride through testing, islanded operation, power-flow analysis, |  | ac | [13 empty] | REF6, REF7
7 | CIGRE LV | This European test system includes three 0.4-kV distribution feeders for commercial, residential, and industrial consumption. This network has also been proposed by CIGRE WG C6-04 for integrating renewable resources to low-voltage (LV) distribution systems.
8 | CIGRE Nordic 32 | Driven by Swedish and Nordic power grids, this test system was developed for voltage security analysis under IEEE Power & Energy Task Force Technical Report 19 |  | 13,220,400 | AC-DC | 74 | 20 | 11060, NA | LT voltage stability |  |  | ms to sec | [5 empty] | REF11
9 | CIGRE HVDC | Developed in 1985, this was the first CIGRE HVdc test system. This system is a monopole with ±500 kV and 12-pulse rectifiers and inverters connected to two ac grids
10 | ENTSOE SPD standard machine controls | three simple test cases implemented by SG SPD to ensure similar behaviour of standard models for machines, their controllers and other elements as well as to introduce consistent standards regarding simulation and element parameters. |  | 21; 400 | ac | 1 | 1 | 475; 76 | transient stability |  |  | ms to some sec | voltage step (test 1), load step (test 2), three phase grid fault (test 3) | standard synchronous machine model - governor: GOVSTEAM0 - excitation/AVR : excSEXS - PSS : PSS2A - ideal transformer without saturation - ideal switches - constant impedance load - infinite source | dynawo : https://github.com/dynawo/dynawo/tree/master/examples/DynaSwing/ENTSOE |  |  | REF9
11 | grid forming grid following test case (4-VSC system) | presents three test cases that simulate a 5-machine all-converter-interfaced power system. Two converters are grid following and use the WECC WTG4A model presented above and three converters are grid forming converters INF, HVDC1 and HVDC2 using a droop control |  | 400; 225; 66 | ac and dc | 10 | 2 | 6,4;? | transient stability |  |  | ms to some sec | disconnection of line (case1), three phase fault (case 2), double step variations on WT and HVDC active powers | - WECC WT with grid following - WECC WT with droop grid forming (INF, HVDC1, HVDC2) - AC line and cables | dynawo : https://github.com/dynawo/dynawo/tree/master/examples/DynaSwing/GridForming_GridFollowing
12 | kundur two-area system | Example from the book 'Power System Stability and Control', written by P. Kundur. It is a test case used for studies on dynamic stability, power interchange, oscillation damping, etc. The two areas are connected with weak tie lines |  |  | ac | 11 | 4 | 2 | frequency stability, small signal stability | [5 empty] | (DPsim) | simpowersystems (DPsim) |  | REF10
13
14
15
16
REF1 | Power systems test case archive.” Accessed on: Feb 25, 2019. [Online]. Available: http://labs.ece.uw.edu/pstca/
REF2 | “IEEE benchmarks.” Accessed on: Feb. 25, 2019. [Online]. Available: h t t p s: // h vd c . c a / knowledge -base/topic:51/v
REF3 | Electric grid test cases.” Accessed on: Feb. 25, 2019. [Online]. Available: https://electricgrids.engr.tamu.edu/electric-grid-test-cases/
REF4 | R . D. Zimmerman, C. E. Murillo-Sanchez, and R. J. Thomas, “MATPOWER: Steady-state operations, planning, and analysis tools for power systems research and education,” IEEE Trans. Power Syst., vol. 26, no. 1, pp. 12–19. Accessed on: Feb. 25, 2019. [Online]. Available: http://ieeexplore .ieee.org/document/5491276/
REF5 | T. K. Vrana, Y. Yang, D. Jovcic, S. Dennetière, J. Jardini, and H. Saad, “The CIGRE B4 DC grid test system,” CIGRE Electra, vol. 270, no. 9, pp. 10–19, 2013.
REF6 | K. Strunz, N. Hatziargyriou, and C. Andrieu, Benchmark Systems for Network Integration of Renewable Energy Resources: CIGRE Task Force C 6.0402, vol. 78, Paris, France: CIGRE, 2009, pp. 1–6.
REF7 | CIGRE, Benchmark Systems for Network Integration of Renewable and Distributed Energy Resources: Task Force TF-C6.04, vol. 575, Paris, France: CIGRE, 2014, pp. 1–119.
REF8 | L. T. G. Lima et al., “IEEE PES task force on test systems for voltage stability analysis and security assessment,” Tech. Rep. TR-19, 2015.
REF9 | 131127_Controller_Test_Report.pdf (entsoe.eu)
REF10 | P. Kundur, N. J. Balu, and M. G. Lauby, Power system stability and control, vol. 7. McGraw-hill New York, 1994
REF11 | S. Peyghami, P. Davari, M. Fotuhi-Firuzabad and F. Blaabjerg, "Standard Test Systems for Modern Power System Analysis: An Overview," in IEEE Industrial Electronics Magazine, vol. 13, no. 4, pp. 86-105, Dec. 2019, doi: 10.1109/MIE.2019.2942376.

## Simulations_tools
Simulation tool name & Models library | phasor or EMT | Open source details | Known limitations | Owner/developer
openmodelica | both | library, simulator, and solvers are opensource | slow on large power systems | Open Source Modelica consortium
dynawo | phasor | models library, simulator and solvers are opensource |  | RTE
DPSim | phasor , DP and EMT | models library, simulator and solvers are opensource |  | RWTH Aachen
RAMSES | phasor | library is opensource |  | ULiège
EMTP-RV | EMT | commercial |  |  | TUD license
PSCAD | EMT | commercial |  | Manitoba Hydro International | TUD license
Powerfactory | both | commercial |  | DIgSILENT GmbH | TUD license | RWTH license
PSS/E | phasor | commercial |  | siemens
NEPLAN | both | commercial |  | NEPLAN AG
RSCAD (RTDS) | EMT (real-time) | commercial |  | RTDS | TUD license | RWTH license
RT-Lab (OPAL-RT) | both (real-time) | commercial |  | OPAL-RT | TUD license | RWTH license
Typhoon | EMT (real-time) | commercial |  | Typhoon | TUD license
simpowersystems- MATLAB Toolbox | both | library is opensource |  | HydroQuébec
Power System Analysis Toolbox (PSAT) - MATLAB Toolbox | phasor | library is opensource |  | Prof. Federico Milano
power dynamics | EMT | library is opensource |  | TUD

## Component models
Component ID | Component full name | description | reference | implementation